# SOP-BH-04: Forced Draft Fan FD-2 Operation & Care

Equipment Tag: FD-2  |  Location: Boiler House, next to Boiler B-3

# Routine Care

Lubricate FD-2 drive-end and non-drive-end bearings every 500 running hours using Grade EP-2 grease. Record in the maintenance register.

Check belt tension weekly. Inspect impeller for ash build-up monthly.

# Operating Limits

Bearing temperature: 75°C (alarm), 90°C (trip)

Motor current: 120 A (alarm), 140 A (trip)

# Startup Interlocks

FD-2 must be running before boiler B-3 fuel firing is permitted. Loss of FD-2 trips B-3 per IBR interlock requirements.